## Sheet1
Inverter
No of inverters | 126
Min Input Voltage | 650 | V
Max Input Voltage | 1500 | V
Max Input Current | 150 | A
Nominal Output Power | 116000 | W
Peak Input Power | 220000 | W
String Connections | 6
Module
Nominal Module Power | 340 | W
Module short circuit current | 9.75 | A
MPP current | 8.95 | A
MPP voltage | 37.84 | V
Open circuit voltage | 44.95 | V
MIN # of panels per string | 13
MAX # of panels per string | 31
MAX # of strings per MPPT | 11
Number of modules per string | 30
Number of parallel strings used | 1386
Number of parallel strings per MPPT used | 3
String power rating | 10200 | W
system power rating | 14137200 | W
minimum recorded temperature | 17 | oC
maximum recorded temperature | 30 | oC
maximum average irradiance | 1250 | W/m2
STC temperature | 25 | oC
STC irradiance | 1000 | W/m2
Tadder | 25 | oC
Temperature
Voc temp coeff | -0.33 | %/oC
Vm temp coeff | -0.36 | %/oC
Isc temp coeff | 0.1 | %/oC
Pm temp coeff | -0.23 | %/oC
String Voc | 1348.5 | V
String Vm | 1135.2 | V
System Voc at low temp | 1385 | V
System Vm at high temp | 1013 | V
Max Isc under max S and high temp | 38 | A
Peak input power at max S and min temp Overall | 17996656 | W
Peak power at s max for each inverter | 114264.4825
Requirement | Good | Vocmax < Vdc_max_inverter
Requirement | Good | Vmmin > Vdc_min inverter
Requirement | Good | Iscmax < Idcmax
Requirement | Good | Pdcmax < Pdc_max_inverter